CGB RESIDENTIAL PV SYSTEM INSPECTION REPORT

Failed Report - Check Here:  ☐ 		 Pending Monitoring - Check Here:  ☐

INSPECTOR: Click here to enter text.		DATE OF INSPECTION:  Click here to enter text.

CUSTOMER NAME: Click here to enter text.	TOWN: Click here to enter text.

RPV#:	Click here to enter text.			INSTALLER: Click here to enter text.

SYSTEM DESIGN FACTORS

If All Factors Verified, Check Here:  ☐

AZIMUTH VERIFIED? YES ☐ NO ☐		IF NOT, CORRECT AZIMUTH: Degrees °

TILT VERIFIED? YES ☐ NO ☐			IF NOT, CORRECT TILT: Degrees °

# OF ARRAYS VERIFIED? YES ☐ NO ☐		# OF PANELS VERIFIED: YES ☐ NO ☐

IF NOT, CORRECT # PANELS / ARRAYS: Click here to enter text.

SHADING VERIFIED?  YES ☐ NO ☐

IF NOT, CALCULATED SHADING (% Solar Access):

Jan:  % Feb:  % Mar:  %Apr:  % May:  % Jun:   % Jul:  % Aug:  % Sep:  % Oct:   %Nov:   %  Dec:  %

PANEL MFR / MODEL VERIFIED? YES ☐ NO ☐  (If available)

IF NOT, CORRECT MFR. / MODEL: Click here to enter text.

INVERTER VERIFIED? YES ☐ NO ☐		IF NOT, CORRECT INVERTER? Enter Text

ADDITIONAL COMMENTS: Click here to enter text.

PERFORMANCE DATA

INSTANTANEOUS POWER WATTS (AC): Click here to enter text.

PRODUCTION (VIA LOCAL PRODUCTION METER): Click here to enter text. KWh

UTILITY METER PURCHASED: Click here to enter text. kWh

UTILITY METER SOLD: Click here to enter text. kWh

OPTIONAL

IRRADIANCE (Watts / m2): Click here to enter text.

TEMPERATURE (oF): Click here to enter text.

CGB POST-INSTALLATION CHECKLIST FOR RESIDENTIAL PV INSTALLATIONS

(Check P/F or indicate N/A – Not Applicable)

|  | Pass | Fail | Suggested | Notes |
| --- | --- | --- | --- | --- |
| PV ARRAY(S) |  |  |  |  |  |
| PV modules secured to mounting structure |  |  |  |  |  |
| PV cables protected and secured |  |  |  |  |  |
| Structural shading (chimneys, arrays, etc)? |  |  |  |  |  |
| Each module & metal mounting structure properly grounded? |  |  |  |  |  |
| Conduit ends weather resistant or junction box with strain relief connectors? |  |  |  |  |  |
| No visible damage to modules, junction boxes or wires |  |  |  |  |  |
| All wiring and conduit is neat and well supported |  |  |  |  |  |
| Array(s) meet 2018 CSBC fire access pathway req. |  |  |  | CT State BC. Sec: 324 |  |
| OVERCURRENT PROTECTION (DC) |  |  |  |  |  |
| Fuses/circuit breakers properly configured |  |  |  |  |  |
| Overcurrent protection correctly rated to not exceed wires ampacity? |  |  |  |  |  |
| User-accessible fuses – no volts at both ends? |  |  |  |  |  |
| DC voltage and current ratings clearly marked on overcurrent protection |  |  |  |  |  |
| DC DISCONNECTS |  |  |  | N.E.C.690.53, 690.7, 690.8 |  |
| PV Disconnect label Operating Current (Imp) Operating Voltage (Vmp) Max System Voltage (Voc – coldest temp.) Short-circuit current (continuous) |  |  |  |  |  |
| Label any fuse or circuit breaker that can be energized in either direction |  |  |  |  |  |
| DC disconnects properly accessible |  |  |  |  |  |
| OVERCURRENT PROTECTION (AC) |  |  |  |  |  |
| Overcurrent protection correctly rated to not exceed wires ampacity? |  |  |  |  |  |
| Fuses/circuit breakers properly configured |  |  |  |  |  |
| AC DISCONNECTS |  |  |  | N.E.C. 690.56(B), 705.10 |  |
| AC Point of Connection Maximum AC operating current Operating voltage |  |  |  |  |  |
| Directory for all system disconnect and notice of multiple sources of power (suitable) |  |  |  |  |  |
| AC disconnects properly accessible |  |  |  |  |  |
| Label any fuse or circuit breaker that can be energized in either direction |  |  |  |  |  |
| INVERTER / INTERCONNECTION |  |  |  |  |  |
| Connected to dedicated branch circuit, line or load side or service, with appropriate back-fed overcurrent protection |  |  |  |  |  |
| SUPPLY SIDE INTERCONNECTION |  |  |  |  |  |
| Service rated enclosure |  |  |  |  |  |
| Disconnects grouped |  |  |  |  |  |
| Proper bonding of metal enclosures |  |  |  |  |  |
| Overcurrent protection |  |  |  |  |  |
|  | Pass | Fail | Suggested | Notes |  |
| OTHER OBSERVATIONS |  |  |  |  |  |
| Consistent with manufacturer specifications? |  |  |  |  |  |
| Homeowner packet including: |  |  |  |  |  |
| - “As-built” system diagram |  |  |  |  |  |
| - homeowner’s manuals |  |  |  |  |  |
| -spec sheets/manuals on major components |  |  |  |  |  |
| -Instructions for system shut-off provided? |  |  |  |  |  |
| E-1 / PV-1 License # resp. for install |  |  |  | ELC. |  |
| E-1 License # resp. for interconnect |  |  |  | ELC. |  |
| SOLAR REPORTING |  |  |  |  |  |
| Remote Monitoring Device Installed |  |  |  |  |  |
| Remote Monitoring Device Operational |  |  |  |  |  |
| Customer ability to access data |  |  |  |  |  |
| Manufacturer of Device (i.e. Locus, etc.) |  |  |  |  |  |
| Model #: |  |  |  |  |  |
| Mac lD or Enphase System ID #: |  |  |  |  |  |
| If microinverter or optimizer, verify communication to all modules |  |  |  |  |  |
| BACKUP POWER – GENERATOR |  |  |  | NEC 702.4(B)(1), 702.7 |  |
| Generator and PV are isolated (incl. manual transfer) or rated for parallel operation? |  |  |  |  |  |
| Transfer instructions label included? |  |  |  |  |  |
| BACKUP POWER – BATTERY |  |  |  |  |  |
| Manufacturer and Model # |  |  |  |  |  |
| Bank capacity (batteries x battery voltage x battery amp-hrs @ 20 - 24hr rate) |  |  |  |  |  |
| Enclosure: |  |  |  |  |  |
| Proper Ventilation |  |  |  |  |  |
| Live parts guarded |  |  |  |  |  |
| Corrosion resistant / non-conductive |  |  |  |  |  |
| Wiring and OCPD | ----- |  |  |  |  |
| Wiring protected and secured | ----- |  |  |  |  |
| Cables are (UL) Listed |  |  |  |  |  |
| - OCPD has high interrupt current rating |  |  |  |  |  |
| - Labeling |  |  |  |  |  |
| - Hazard: GF, Fire, Corrosive Chemical |  |  |  |  |  |
| Voltage and current ratings |  |  |  |  |  |
| - Backup equipment ID label |  |  |  |  |  |

Additional Notes / Concerns: (i.e. snow concerns, gutter overhang, Date of Installation Label, Label durability) : Click here to enter text. 
CGB accepted methodology for calculating values for labels:

PV disconnect label = refer to NEC (690.53)

Operating current = Imp x # parallel strings

Operating voltage = Vmp x # series modules in the strings

Max system voltage (based on coldest temp. on record) = Vox x # series modules in the strings x temperature correction (from NEC table (690.7) or manufacturer’s instructions)

Short-circuit current: = Isc x #parallel strings x 1.25 safety factor (NEC 690.8)

AC disconnect label = refer to NEC (690.54)

____________________________		_______

Inspector signature				Date

___________________________		_________

CGB Review					Date

____________________________		________

Installer signature				Date

REQUIRED PHOTOS:

ARRAY(S)

INVERTER (IF NOT MICROINVERTERS)

WIRE MANAGEMENT/CONDUIT RUNS

ARRAY UNDERSIDE

MONITORING PDP/MAC ID

LABELING

ELECTRICAL PANEL / BREAKERS

DISCONNECT(S)

RECOMMENDED FOR SELF-INSPECTION (REQUIRED FOR THIRD-PARTY):

SITE SURVEY PHOTOS (E.G., PATHFINDER, COMPASS, ETC)